## Residential HVAC
| Residential projects QC checklist | Checked | N/A | comments
Version date 10/29/2019
| QC review by: | input name
Equipment
1 | Check if equipment is sized properly
As rule of the thumb use 500-600 sf/ton ratio (400-500 for very warm climates like climate zones with summer design DB temperatures above 100 deg F). Otherwise check MJDS. For Rec. centers 400 sf/ton
2 | Check if Mechanical plans and T24 report are coordinated.
EER/SEER and AFUE needs to match. Use only AHRI rated values
3 | Check T24 if Quiet cool fans needed. We do need to show them in our mech plans due the space constrain.
4 | Check if equipment location allows enough room and clearances.
For attic FAU's check if there is at least 30 inches above platform and 30 inches in front of the FAU. Check if access path is less than 20 ft and accessible.
For vertical FAU's verify cabinet space. Preferable is 40x40"
For ducted Fan Coils in soffit check available clear soffit space and consider condensate pipe with slope.
Check condensers/heat pump clearances (in San Diego min 4 ft from property line)
5 | If any equipment is located at the roof level - show permanent roof access. Put note next to stairs or other access shown on arch. background
6 | Show attic access and platform (for attic mounted FAU's). No duct shall be on pathway or platform.
7 | In case of multiple condensers / heat pums (typical for multifamily projects) , associate all outdoor with belonging FAU / FC. Best way is to put apartment unit # next to CU tag.
8 | For typical tract home, it is safe to locate the CU in the backyard because the side yard limitation. Unless told by the developer.
9 | Check if project locations requires low NOx furnaces. Specify equipment accordingly
Air-conditioning
1 | Call out and show on the plans primary condensate lines.
2 | If FAU/FC is installed in attic or above ceiling or any other concealed (furred space) call out and show secondary condensate line (optionally call out overflow switch). Keynote # 3
All condensate receptors shall be located in general area accessible to occupant / user
3 | Check for any conflicts and allow condensate line slope (1/4" : 12" or 2%)
4 | No flex duct shall penetrate rated wall, ceiling or floor
5 | For non residential buildings and zones use only rigid ducts. Max 5 ft connectors are allowed.
Verify if return air sizing complies with residentioal compliance manual sizing tables (T4-10 and 4-11) if possible or stay as much close to these sizes.
If not possible have at least 2 return grilles (one for main zone and one for master bedroom area)
For two stories homes prefer to have 3rd return ducted to 1st floor.
6 | Return air can't be located in kitchen.
7 | For retail (commercial) spaces within multifamily building use only rigid ducts
8 | Check and cover all process loads in elevator controll rooms, pump rooms, electrical rooms, inverter rooms, IDF rooms, etc.
Ventilation
1 | Show ventilation calculation on M-0.2 for each single family and multifamily apartment unit.
Ventilation rates are as follows:
CFM=0.01 * SQFT + 7.5 * (No. of Bedrooms + 1) (for Single Family per CEC 150.0(o) and ASHRAE 62.2)
CFM=0.03 * SQFT + 7.5 * (No. of Bedrooms + 1) (for Low-rise Multi-Family per CEC 150.0(o) and ASHRAE 62.2)
CFM=0.06 * SQFT + 5 * (No. of Bedrooms + 1) (for High-rise Multi-Family per CEC 120.1(b)2 and CBC)
2 | Make sure proper code is called out on ventilation calc. table (per item above)
3 | Design at least one continuous fan for whole house ventilation - mark as continuous on fan schedule and indicate on plans (in most cases keynote 5)
4 | Continuous fan for whole house ventilation shall be listed and have sound rating less than 1 sone
5 | Provide ventilation in any trash room and/or janitor closet (1 cfm/ft2)
6 | Provide ventilation in any storage room (1.5 cfm/ft2)
Corridor ventilation
1 | Provide corridor ventilation. OSA=0.15 cfm/sf. EA = 0.7 x OSA. All other exhausts that uses corridor for makeup air should be taken in count as EA in previous equation.
2 | Provide combination fire smoke dampers (FSD's) at all duct penetrations through rated shaft or ceilings
3 | Verify shaft sizes including necessary room for FSD's sleeve (typically 18")
4 | Verify that complete corridor area is covered with ventilation and there is no closed doors or other obstacles on air path.
5 | Rooms adjacent to corridor shall not draw air from corridor or transfer air from corridor.
Exhaust
1 | Design local exhaust for all bathrooms, restrooms and kitchen hoods
2 | Provide exhaust fan with humidistat for bathroom
3 | Call out door undercut for all rooms with exhaust
Verify local exhaust termination clearances (3 ft from operable portions of windows and doors and property line. 10 ft from OSA intakes. This does not apply for garage or commercial kitchen exhausts)
Laundry
1 | Check if lint duct is max. 14ft long including two elbows. Exceptions:
If dryer model is known and manufacturer allows longer runs - attach dryer cut sheets on plans
If dryer model is not known show booster fan on the plans
2 | Provide (and call out on plans) access pannel for booster fan (if used).
3 | Provide makeup air for laundry. (show opening and keynote #9 on the plans)
For residential dryers - 100 sq. in . Clear opening
For nonresidential dryers - 1 sq. in . Per 1000 BTUH of input rating of dryers (default 35,000 MBTUH)
4 | Provide ventilation for laundry rooms (other than closet type)
For residential projects whole house fan in laundry
For nonresidential projects exhaust rate per CEC (0.15 cfm / sf)
5 | Show buster fans on mechanical schedule and tag them on the floorplans.
Coordination
1 | Verify ducts routing with structural. No ducts over the walls, studs and through beams
2 | Check for conflicts with plumbing (water, gas, vents and waste verticals)
3 | Check for conflicts with electrical (i.e. no ducts should be routed over el. panels)
4 | Check for conflicts with lightning (coodinate registers and light layout)
5 | Show water heater vent on M plans
6 | Verify if WH vent complies with code and manufacturer recommendation.
7 | Verify if plans reffers to appropriate (current) cycle