## FIXTURE UNIT CALCS TABLE
FIXTURE UNIT CALCULATION
FIXTURE TYPE | QTY | DEMAND WEIGHT IN WSFU | [5 empty] | DRAINAGE
|  | FIXTURE DEMAND | HOT OR 75% | COLD OR 75% | TOTAL SUPPLY DEMAND | TOTAL HOT WATER DEMAND | TOTAL COLD WATER DEMAND | DFU | TOTAL | Hide Row if QTY=0
BATHTUB | 0 | 4 | 3 | 3 | 0 | 0 | 0 | 2 | 0 | TRUE
BATHTUB FILL VALVE | 0 | 10 | 7.5 | 7.5 | 0 | 0 | 0 | 2 | 0 | TRUE
BIDET | 0 | 1 | 0.8 | 0.8 | 0 | 0 | 0 | 1 | 0 | TRUE
CLOTHES WASHER | 0 | 4 | 3 | 3 | 0 | 0 | 0 | 3 | 0 | TRUE
DISHWASHER | 0 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | N/A | 0 | TRUE
DRINKING FOUNTAIN | 0 | 0.5 | 0 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | TRUE
WATER COOLER | 0 | 0.5 | 0 | 0.5 | 0 | 0 | 0 | 0.5 | 0 | TRUE
PRIMARY HOSE BIB | 0 | 2.5 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | TRUE
ADDITIONAL HOSE BIB | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | TRUE
LAVATORY | 0 | 1 | 0.8 | 0.8 | 0 | 0 | 0 | 1 | 0 | TRUE
KITCHEN SINK | 0 | 1.5 | 1.2 | 1.2 | 0 | 0 | 0 | 2 | 0 | TRUE
BAR SINK | 0 | 1 | 0.8 | 0.8 | 0 | 0 | 0 | 1 | 0 | TRUE
LAUNDRY SINK | 0 | 1.5 | 1.2 | 1.2 | 0 | 0 | 0 | 2 | 0 | TRUE
MOP SINK | 0 | 1.5 | 1.2 | 1.2 | 0 | 0 | 0 | 3 | 0 | TRUE
SHOWER, PER HEAD | 0 | 2 | 1.5 | 1.5 | 0 | 0 | 0 | 2 | 0 | TRUE
URINAL, FLUSH TANK | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | TRUE
URINAL, FLUSH VALVE | 0 | 4 | 0 | 3 | 0 | 0 | 0 | 2 | 0 | TRUE
WASH FOUNTAIN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
WATER CLOSET, FLUSH TANK | 0 | 2.5 | 0 | 2.5 | 0 | 0 | 0 | 3 | 0 | TRUE
WATER CLOSET, FLUSH VALVE | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 3 | 0 | TRUE
FLOOR DRAIN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | TRUE
FLOOR DRAIN, EMERGENCY | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
FOOD WASTE DISPOSER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | TRUE
LAWN SPRINKLER, PER HEAD | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | TRUE
MOBILE HOME | 0 | 12 | 9 | 9 | 0 | 0 | 0 | 6 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
(FOR EXTRA FIXTURE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TRUE
TOTAL FIXTURE UNITS |  |  |  |  | 0 | 0 | 0 | DFU'S | 0
EQUIVALENT WATER DEMAND IN GPM |  |  |  |  | 1 | 1 | 1
REQUIRED MINIMUM WASTE PIPE SIZE | [8 empty] | 1-1/4"

## HOT WATER DEMAND (2015 ASHRAE)
BUILDING HOT WATER DEMAND FIXTURE UNIT CALCULATION (PER 2015 ASHRAE HVAC TABLE 16 AND FIGURE 27)
FIXTURE TYPE | QTY | DEMAND WEIGHT IN WSFU
|  | FIXTURE DEMAND | TOTAL SUPPLY DEMAND

## FIXTURE UNIT REF TABLE
FIXTURE TYPE | FIXTURE DEMAND | HOT OR 75% | COLD OR 75% | DFU
ADDITIONAL HOSE BIB | 1 | 0 | 1 | 0
BAR SINK | 1 | 0.8 | 0.8 | 1
BATHTUB | 4 | 3 | 3 | 2
BATHTUB FILL VALVE | 10 | 7.5 | 7.5 | 2
BIDET | 1 | 0.8 | 0.8 | 1
CLOTHES WASHER | 4 | 3 | 3 | 3
DISHWASHER | 1.5 | 1.5 | 0 | N/A
DRINKING FOUNTAIN | 0.5 | 0 | 0.5 | 0.5
FLOOR DRAIN | 0 | 0 | 0 | 3
FLOOR DRAIN, EMERGENCY | 0 | 0 | 0 | 0
FOOD WASTE DISPOSER | 0 | 0 | 0 | 3
KITCHEN SINK | 1.5 | 1.2 | 1.2 | 2
LAUNDRY SINK | 1.5 | 1.2 | 1.2 | 2
LAVATORY | 1 | 0.8 | 0.8 | 1
LAWN SPRINKLER, PER HEAD | 1 | 0 | 1 | 0
MOBILE HOME | 12 | 9 | 9 | 6
MOP SINK | 1.5 | 1.2 | 1.2 | 3
PRIMARY HOSE BIB | 2.5 | 0 | 2.5 | 0
SHOWER, PER HEAD | 2 | 1.5 | 1.5 | 2
SINK | 1.5 | 1.2 | 1.2 | 2
URINAL, FLUSH TANK | 2 | 0 | 2 | 2
URINAL, FLUSH VALVE | 4 | 0 | 3 | 2
WASH FOUNTAIN
WATER CLOSET, FLUSH TANK | 2.5 | 0 | 2.5 | 3
WATER CLOSET, FLUSH VALVE | 5 | 0 | 5 | 3
WATER COOLER | 0.5 | 0 | 0.5 | 0.5
HUB DRAIN
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)
(FOR EXTRA FIXTURE)

## FIXTURE UNITS VS GPM CONVERSION
FIXTURE UNITS |  | FLOW
FLUSH TANK | FLUSH VALVE | GPM
0 |  | 1
1 |  | 2
3 |  | 3
4 |  | 4
6 |  | 5
7 |  | 6
8 |  | 7
10 |  | 8
12 |  | 9
13 |  | 10
15 |  | 11
16 |  | 12
18 |  | 13
20 |  | 14
21 |  | 15
23 |  | 16
24 |  | 17
26 |  | 18
28 |  | 19
30 |  | 20
32 |  | 21
34 | 5 | 22
36 | 6 | 23
39 | 7 | 24
42 | 8 | 25
44 | 9 | 26
46 | 10 | 27
49 | 11 | 28
51 | 12 | 29
54 | 13 | 30
56 | 14 | 31
58 | 15 | 32
60 | 16 | 33
63 | 18 | 34
66 | 20 | 35
69 | 21 | 36
74 | 23 | 37
78 | 25 | 38
83 | 26 | 39
86 | 28 | 40
90 | 30 | 41
95 | 31 | 42
99 | 33 | 43
103 | 35 | 44
107 | 37 | 45
111 | 39 | 46
115 | 42 | 47
119 | 44 | 48
123 | 46 | 49
127 | 48 | 50
130 | 50 | 51
135 | 52 | 52
141 | 54 | 53
146 | 57 | 54
151 | 60 | 55
155 | 63 | 56
160 | 66 | 57
165 | 69 | 58
170 | 73 | 59
175 | 76 | 60
185 | 82 | 62
195 | 88 | 64
205 | 95 | 66
215 | 102 | 68
225 | 108 | 70
236 | 116 | 72
245 | 124 | 74
254 | 132 | 76
264 | 140 | 78
284 | 158 | 82
294 | 168 | 84
305 | 176 | 86
315 | 186 | 88
326 | 195 | 90
337 | 205 | 92
348 | 214 | 94
359 | 223 | 96
370 | 234 | 98
380 | 245 | 100
406 | 270 | 105
431 | 295 | 110
455 | 329 | 115
479 | 365 | 120
506 | 396 | 125
533 | 430 | 130
559 | 460 | 135
585 | 490 | 140
611 | 521 | 145
638 | 559 | 150
665 | 596 | 155
692 | 631 | 160
719 | 666 | 165
748 | 700 | 170
778 | 739 | 175
809 | 775 | 180
840 | 811 | 185
874 | 850 | 190
945 | 931 | 200
1018 | 1009 | 210
1091 | 1091 | 220
1173 | 1173 | 230
1254 | 1254 | 240
1335 | 1335 | 250
1418 | 1418 | 260
1500 | 1500 | 270
1583 | 1583 | 280
1668 | 1668 | 290
1755 | 1755 | 300
1845 | 1845 | 310
1926 | 1926 | 320
2018 | 2018 | 330
2110 | 2110 | 340
2204 | 2204 | 350
2298 | 2298 | 360
2388 | 2388 | 370
2480 | 2480 | 380
2575 | 2575 | 390
2670 | 2670 | 400
2765 | 2765 | 410
2862 | 2862 | 420
2960 | 2960 | 430
3060 | 3060 | 440
3150 | 3150 | 450
3620 | 3620 | 500
4070 | 4070 | 550
4480 | 4480 | 600
5380 | 5380 | 700
6280 | 6280 | 800
7280 | 7280 | 900

## DRAINAGE PIPE SIZING TABLE
2% SLOPE | 1% SLOPE | NOMINAL PIPE DIAMETER
1 |  | 1-1/4"
1 |  | 1-1/2"
8 |  | 2"
14 |  | 2-1/2"
35 |  | 3"
216 | 172 | 4"
428 | 342 | 5"
720 | 576 | 6"
2640 | 2112 | 8"

## BACKWATER VALVE CALCULATIONS
| 15 | 17 | 13 | 13 | 13 | 13 | 13 | 13 | 13
[10 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 25% | 25% | 25% | 25%
PROJECT DEVELOPER
ADDRESS
ADDRESS
ADDRESS
# UNITS
| DATE | [6 empty] | This color cell requires data input→
Section 710.0 Backflow Protection (Is it required for this sewer POC)
22 | Sewer POC's |  | Upstream Manhole |  | Downstream Manhole |  | Owners Required Safety Factor Exceeding Section 710 (0'-6") | Protection Required
80 | Building or POC No. | FF Elevation at Plumbing Fixtures | Rim Elevation | Elevation Differential from FF | Rim Elevation | Elevation Differential from FF |  | Elevation Differential from FF with Safety Factor | Yes or NO
| Building 1 | 362.02 | 360.83 | 1.19 | 361.06 | 0.96 | 0.5 | 0.69 | NO
| Building 2 | 362.32 | 361.23 | 1.09 | 361.38 | 0.94 | 0.5 | 0.59 | NO
| Building 3 | 361.87 | 361.38 | 0.49 | 362.44 | -0.57 | 0.5 | -0.01 | YES
| Building 4 | 364.97 | 364.06 | 0.91 | 364.29 | 0.68 | 0.5 | 0.41 | NO
| Building 5 | 365.52 | 364.06 | 1.46 | 364.29 | 1.23 | 0.5 | 0.96 | NO
| Building 6 | 366.62 | 366.04 | 0.58 | 366.48 | 0.14 | 0.5 | 0.08 | NO
| Building 7 | 367.77 | 366.04 | 1.73 | 366.48 | 1.29 | 0.5 | 1.23 | NO
| Building 8 | 368.67 | 367.16 | 1.51 | 367.68 | 0.99 | 0.5 | 1.01 | NO
| Building 9 | 368.97 | 367.82 | 1.15 | 367.68 | 1.29 | 0.5 | 0.65 | NO
| Building 10 | 367.8 | 367.68 | 0.12 | 366.48 | 1.32 | 0.5 | -0.38 | YES
| Building 11 | 367.42 | 367.68 | -0.26 | 366.48 | 0.94 | 0.5 | -0.76 | YES
| Building 12 | 366.42 | 366.48 | -0.06 | 365.14 | 1.28 | 0.5 | -0.56 | YES
| Building 13 | 365.52 | 364.29 | 1.23 | 363.17 | 2.35 | 0.5 | 0.73 | NO
| Building 14 | 364.52 | 364.06 | 0.46 | 364.29 | 0.23 | 0.5 | -0.04 | YES
| Clubhouse | 372.67 | 372.67 | 0 | 372 | 0.67 | 0.5 | -0.5 | YES
| Exercise | 372.67 | 372.67 | 0 | 372 | 0.67 | 0.5 | -0.5 | YES
| Maintenance | 367.92 | 372 | -4.08 | 367.62 | 0.3 | 0.5 | -4.58 | YES

## BOILER SYSTEM SIZING (APTS.)
Boiler System Sizing (2015 ASHRAE HANDBOOK)
[7 empty] | 130 or more Apts. |  | 100 Apts. |  | 75 Apts. |  | 50 Apts. |  | 20 or fewer Apts.
[7 empty] | Storage Capacity | Recovery Capacity | Storage Capacity | Recovery Capacity | Storage Capacity | Recovery Capacity | Storage Capacity | Recovery Capacity | Storage Capacity | Recovery Capacity
[7 empty] | 3 | 4.5 | 3 | 6.4 | 3 | 7.9 | 3 | 9.2 | 3 | 11.1
[7 empty] | 6 | 3.9 | 6 | 5.6 | 6 | 7.1 | 6 | 8.4 | 6 | 10.2
[7 empty] | 9 | 3.4 | 9 | 5 | 9 | 6.2 | 9 | 7.6 | 9 | 9.2
[7 empty] | 12 | 3 | 12 | 4.4 | 12 | 5.6 | 12 | 6.8 | 12 | 8.3
[7 empty] | 15 | 2.6 | 15 | 3.9 | 15 | 4.9 | 15 | 6.1 | 15 | 7.6
[7 empty] | 18 | 2.3 | 18 | 3.4 | 18 | 4.4 | 18 | 5.5 | 18 | 6.8
[7 empty] | 21 | 2.2 | 21 | 3.1 | 21 | 3.9 | 21 | 4.9 | 21 | 6.2
[7 empty] | 24 | 2.1 | 24 | 2.8 | 24 | 3.6 | 24 | 4.5 | 24 | 5.6
[7 empty] | 27 | 2.1 | 27 | 2.6 | 27 | 3.3 | 27 | 4.1 | 27 | 5.1
[7 empty] | 30 | 2.1 | 30 | 2.5 | 30 | 3 | 30 | 3.8 | 30 | 4.6
[7 empty] | 33 | 2.1 | 33 | 2.5 | 33 | 2.8 | 33 | 3.5 | 33 | 4.2
[7 empty] | 36 | 2.1 | 36 | 2.5 | 36 | 2.8 | 36 | 3.2 | 36 | 3.9
[7 empty] | 39 | 2.1 | 39 | 2.5 | 39 | 2.8 | 39 | 3.1 | 39 | 3.7
[7 empty] | 42 | 2.1 | 42 | 2.5 | 42 | 2.8 | 42 | 3.1 | 42 | 3.5
[7 empty] | 45 | 2.1 | 45 | 2.5 | 45 | 2.8 | 45 | 3.1 | 45 | 3.4
[7 empty] | 48 | 2.1 | 48 | 2.5 | 48 | 2.8 | 48 | 3.1 | 48 | 3.4
Additional Recovery |  |  |  | 0
Total Number of Units |  |  |  | 105
Peak Expected Building Occupants |  |  |  | --
Water Delivery Temperature (°F) |  |  |  | 120
Design Entering Cold-Water Temperature (°F) |  |  |  | 60
Heating Device Thermal Efficiency (%) |  |  |  | 95
*Notes |  | Usable Storage Capacity (gal/apt) | Recovery Capacity (gph/apt) | Tank Size (gal.) | Total Recovery Capacity | Heating Rate Q
A | 20 or Fewer Apts. | 5 | 10.4635 | 750 | 1098.6675 | 582872.0211
B | 50 Apts. | 10 | 7.293 | 1500 | 765.765 | 406258.4842
C | 75 Apts. | 5 | 7.3207 | 750 | 768.6735 | 407801.52
D | 100 Apts. | 6 | 5.6415 | 900 | 592.3575 | 314261.2421
E | 130 or More Apts. | 5 | 4.0979 | 750 | 430.2795 | 228274.5979
*Notes:
A. | For storage capacities over 45 gal/apt, use Recovery Value of 3.4
B. | For storage capacities over 39 gal/apt, use Recovery Value of 3.1
C. | For storage capacities over 33 gal/apt, use Recovery Value of 2.8
D. | For storage capacities over 30 gal/apt, use Recovery Value of 2.5
C. | For storage capacities over 24 gal/apt, use Recovery Value of 2.1